WATERLINE NOTES

- SCWD POSSESSES THE AUTHORITY TO IMPLEMENT FIELD ADJUSTMENTS AS DEEMED NECESSARY, EVEN IF SUCH MODIFICATIONS DEVIATE FROM THE APPROVED PLANS.

- WATERLINES SHOULD BE THE LAST UTILITY INSTALLED UNLESS AUTHORIZED BY WCWD.

- BEFORE ANY INSTALLATION OF WATERLINES, FINAL GRADING MUST BE COMPLETED.

- NO PROPOSED UTILITIES SHALL BE INSTALLED WITHIN 5 FEET ON EITHER SIDE OF THE PROPOSED WATERLINES.

- WATERLINES SHALL HAVE A MINIMUM COVER OF 30 INCHES. ANY WATERLINES 12 INCHES IN DIAMETER OR LARGER SHALL HAVE A MINIMUM COVER OF 48 INCHES.

- ALL WATERLINES SHALL BE DR18 C900 OR DIP WHERE REQUIRED.

- ALL BEDDING AND BACKFILL SHALL BE IN ACCORDANCE WITH SCWD STANDARD SPECIFICATIONS AND 10 STATES STANDARDS.

- INSTALL MECHNICAL JOINT BENDS AS REQUIRED TO LIMIT RADIUS OF WATERLINE CURVATURE TO MANUFACTURER'S REQUIREMENTS OR AS REQUIRED BY SCWD.

- GATE VALVES AT TEES SHALL BE RESTRAINED BY FOSTER ADAPTER OR SOLID SWIVEL.

- ALL CONNECTIONS TO EXISTING WATERLINES SHALL BE PERFORMED BY SCWD APPROVED CONTRACTOR IN ACCORDANCE WITH THE WATERLINE EXTENSION AGREEMENT AT THE CONTRACTOR’S EXPENSE. MATERIALS SHALL BE FURNISHED BY THE CONTRACTOR.

- FOR ANY UTILITY CROSSING BETWEEN WATER, SEWER, FORCEMAIN, AND STORM SEWER WITH A VERTICAL SEPARATION OF LESS THAN 18 INCHES, REFERENCE SCWD STANDARD TYPICAL UTLITY CROSSING DETAIL. SCWD WILL NOT APPROVE UTILITY CROSSINGS THAT HAVE LESS THAN 6 INCHES OF VERTICAL SEPARATION.

- IN AREAS WHERE 1” OR SMALLER SERVICE LINES ARE PROPOSED UNDER SIDEWALKS, DRIVEWAYS, OR PAVEMENT, 2” SCHEDULE 40 PVC CASINGS SHALL BE INSTALLED FOR THE SERVICE LINE.

- FIRE PROTECTION LINES SHALL BE DISINFECTED, TESTED, AND ACCEPTED IN ACCORDANCE WITH SCWD STANDARD SPECIFICATIONS BEFORE BEING PLACED IN SERVICE.

- ALL SERVICE LINES ENDING IN VALVES FOR LARGE METERS SHALL BE RESTRAINED TO THE TEE IN LEIU OF THE INSTALLATION OF A REVERSE CONCRETE ANCHOR (DEADMAN).

- METER INSTALLATIONS ARE TO BE PERFORMED BY SCWD.

- THE PROPOSED PROJECT HAS XXX ZONING, XXX LINEAR FEET OF PROPOSED WATER MAIN, AND XXX WATER METER INSTALLATIONS.